## Slide 1: June 1 Meeting
Summary of Models (MLR, SVM, DTrees)
  accuracy + speed
Train/Validation/Test of each
Dealing with features that are out of calibration themselves
Sensors besides CH1CDWFLO

## Slide 2: Summary of Models
 | Mean Absolute Error using varying amounts of training data on CH1CDWFLO (gpm) |  |  |  | Time (1mo train)
Model | 1 month | 3 months | 6 months | 12 months | 
MLR | 10.27 | 54.46 | 110.77 | 130.55 | 11 ms
SVM | 11.70 | 24.01 | 24.6 | 30.88 | 15 ms
Decision Trees | 14.79 | 42.75 | 51.93 | 61.1 | ~300 ms
LASSO Features | CDWP1SPD', 'CDWP1kW', 'CH1FLA' | ‘CH1S', 'CDWP1SPD' | 'CDWP1SPD', 'CDWP1kW', 'CH1DPLift' | CDWP1SPD', 'CDWP1kW', 'CH1DPLift' | 1.6 s

## Slide 3: MLR - 1 month CDWP1SPD', 'CDWP1kW', 'CH1FLA' Mean Absolute Error in Validation Set: 10.3 gpm

## Slide 4: MLR - 12 months CDWP1SPD', 'CDWP1kW', 'CH1FLA' Mean Absolute Error in Validation Set: 130.6 gpm

## Slide 5: Decision Trees - Picking Tree Depths

## Slide 6: Decision Trees - 1 Month (Tree Depth = 7)
Average Abs Error for Training (Sept 2016) = 14.79 GPM

## Slide 7: Decision Trees - 3 Month (Tree Depth = 6)
Average Abs Error for Training (Sept 2016) = 42.75 GPM

## Slide 8: Decision Trees - 6 Month (Tree Depth = 8)
Average Abs Error for Training (Sept 2016) = 51.93 GPM

## Slide 9: Decision Trees - 12 Month (Tree Depth = 9)
Average Abs Error for Training (Sept 2016) = 61.1 GPM

## Slide 10: SVM - 1 month CDWP1SPD', 'CDWP1kW', 'CH1FLA' Mean Absolute Error in Validation Set: 11.7 gpm

## Slide 11: SVM - 12 months with LASSO features 'CH2CDWFLO', 'CDWP1SPD', 'CDWP1kW', 'CH1DPLift' Mean Absolute Error in Validation Set: 316gpm

## Slide 12: SVM - 12 months without CH2CDWFLO 'CDWP1SPD', 'CDWP1kW', 'CH1DPLift' Mean Absolute Error in Validation Set: 30.9 gpm
Notes: evidence that we need to take into account other sensors drift….. either keeping it as a manual check with validation sets or write in an auto removal of features that have been recorded as out of calibration during the training set

## Slide 13: Ch2 with SVM features = 'CDWP2SPD', 'CT1kW', 'CH2PCTLoad', 'CDWP2kW', 'CH2FLA', 'CDWP2Hz' mean absolute error = 138 gpm

## Slide 14: Next Steps
Package model into more usable form
Unit tests
Figure out how to deal with out of calibration features - or just leave up to the user